## EDT_J1939_DTC_SPNS
SPN (Code in Modbus Register) | FMI | CAT Code | CAT Description | J1939 SPN
51 | -- | -- | -- | Throttle 1 position
52 | 0 | E008(3) | High Aftercooler Temp Shutdown | Engine Intercooler Temperature
52 | 15 | E279(1) | High Aftercooler Temp Warning | Engine Intercooler Temperature
52 | 16 | E007(2) | High Aftercooler Temp Derate | Engine Intercooler Temperature
94 | 1 | E198(3) | Low Fuel Pressure | Engine fuel delivery pressure
95 | 15 | E095(1) | Fuel Filter Restriction Warning | Engine fuel filter differential pressure
99 | 15 | E099(1) | Engine oil filter restriction warning | Engine oil filter differential pressure
100 | 1 | E040(3) | Low Engine Oil Pressure Shutdown | Engine oil pressure
100 | 17 | E100(1) | Low Engine Oil Pressure Warning | Engine oil pressure
101 | 0 | E013(3) | High Crankcase Pressure Shutdown | Engine crankcase pressure
101 | 16 | E012(2) | High Crankcase Pressure Derate | Engine crankcase pressure
101 | 15 | E101(1) | High Crankcase Pressure Warning | Engine crankcase pressure
102 | 15 | E162(1) | High Boost Pressure | Engine intake manifold 1 pressure
102 | 16 | E162(2) | High Boost Pressure | Engine intake manifold 1 pressure
107 | 15 | E272(1) | Inlet Air Restriction Warning | Engine air filter 1 differential pressure
107 | 16 | E031(2) | Air Filter Restriction Derate | Engine air filter 1 differential pressure
108 | 16 | E009(2) | High Altitude Derate | Barometric pressure
110 | 0 | E016(3) | High Engine Coolant Temp Shutdown | Coolant temperature
110 | 15 | E017(1) | High Engine Coolant Temp Warning | Coolant temperature
110 | 16 | E015(2) | High Engine Coolant Temp Derate | Coolant temperature
110 | 17 | E038(1) | Low Engine Coolant Temp Warning | Coolant temperature
111 | 17 | E552(1) | Low Aftercooler coolant level | Engine coolant level
111 | 17 | E552(2) | Low Aftercooler coolant level | Engine coolant level
111 | 17 | E552(3) | Low Aftercooler coolant level | Engine coolant level
111 | 17 | E2143(1) | Low Aftercooler coolant level | Engine coolant level
111 | 17 | E2143(2) | Low Aftercooler coolant level | Engine coolant level
111 | 17 | E2143(3) | Low Aftercooler coolant level | Engine coolant level
158 | 17 | E043(1) | Low System Voltage Warning | Keyswitch battery potential
168 | -- | -- | -- | Battery voltage
172 | -- | -- | -- | Intake mainfold temperature
173 | 15 | E173(1) | High Exhaust Temperature Warning | Engine exhaust gas temperature
173 | 16 | E021(2) | High Exhaust Temperature Derate | Engine exhaust gas temperature
175 | -- | -- | -- | Oil temperature
190 | 0 | E004(3) | Engine overspeed Shutdown | Engine speed
190 | 15 | E190(1) | Engine overspeed warning | Engine speed
632 | -- | -- | -- | Fuel shutoff 1
677 | -- | -- | -- | Engine starter relay
970 | 31 | E264(3) | Emergency Stop Activated | Aux Shutdown Switch
1208 | -- | -- | -- | Oil pressure (unfiltered)
1442 | -- | -- | -- | Fuel valve 1 position
1656 | -- | -- | -- | Auto-Start Enable Switch
3563 | -- | -- | -- | Intake Manifold 1 pressure
4000 | 31 | E2087(3) | Air intake shutoff closed
4289 | -- | -- | -- | Pre-catalyst Temp 1
4290 | -- | -- | -- | Post-catalyst Temp 1
4779 | -- | -- | -- | Differential catalyst temp 1

## J1939 FMI List
List of FMI (Failure Mode Identification) Codes according to SAE standard J1939-73 , Revision 2010-FEB
Code | Description
0 | Data valid but above normal operational range, Most severe
1 | Data valid but below normal operating range, Most severe
2 | Data erratic, intermittent, or incorrect
3 | Voltage above normal, or shorted to high source
4 | Voltage below normal, or shorted to low source
5 | Current below normal or open cirucit
6 | Current above normal or grounded circuit
7 | Mechanical system not responding or out of adjustement
8 | Abnormal frequency or pulse width period
9 | Abnormal update rate
10 | Abnormal rate of change
11 | Root cause not known
12 | Bat intelligent device or component
13 | Out of calibration
14 | Special instructions
15 | Data valid but above normal operating range, least severe level
16 | Data valid but above normal operating range, moderately severe level
17 | Data valid but below normal operating range, least severe level
18 | Data valid but below normal operating range, moderately severe level
19 | Received network data in error
20 | Data drifted high
21 | Data drifted low
31 | Condition exists